{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["fill"],"not_rendered":{"external_links":1,"defined_names":1,"comments":11},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"fill","index":0,"n_rows":53,"n_cols":26,"rows_kept":53,"merged":[[0,8,0,9],[0,10,0,18],[1,0,1,1],[1,2,1,7],[1,8,1,18],[2,0,2,1],[2,2,2,4],[3,0,3,1],[4,0,4,1],[4,2,4,3],[4,7,4,8],[5,0,7,6],[5,7,5,8],[6,7,6,8],[7,7,7,8],[8,0,9,0],[8,1,9,1],[8,2,9,2],[8,3,9,3],[8,4,9,4],[8,5,9,5],[8,6,9,6],[8,7,9,7],[8,8,9,8],[42,0,42,1],[47,0,47,1]],"flags":["formulas_cached_only"]}
["Conduit Fill Computation",{"$nulls":7},"Version 4.4",null,"Copyright 2006-2007 by Designs and Ideas, Inc.    Some rights reserved"]
["Customer:",null,"name",{"$nulls":5},"This work is licensed under the Creative Commons Attribution-ShareAlike License. To view a copy of this license, visit http://creativecommons.org/licenses/by-sa/2.5/ or send a letter to Creative Commons, 559 Nathan Abbott Way, Stanford, California 94305, USA."]
["Job Num:"]
["Rev:",null,0.30000000000000004]
["Date:",null,"2008-03-04",{"$nulls":4},"Use",null,"Mic/line","Video","CAT5e","","","","","","",""]
["This sheet is to aid in figuring what size conduit is needed - or for determining how many cables will fit in a particular size conduit.",{"$nulls":6},"Cable",null,291,815,4245]
[{"$nulls":7},"OD",null,0.131,0.232,{"v":0.20800000000000002,"d":"0.208"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"}]
[{"$nulls":7},"Cable area",null,{"v":0.013478249400000001,"d":"0.013"},{"v":0.0422733696,"d":"0.042"},{"v":0.03397954560000001,"d":"0.034"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"}]
["Start","-","End","Qty","Conduit Size","Conduit Area","Cable Area","Extra Space","Min. size"]
[]
["JP1","-","Pull Box",1,0.5,{"v":0.12154319321914336,"d":"0.12"},{"v":0.1096646166,"d":"0.11"},{"v":0.011878576619143363,"d":"0.0119"},0.5,5,1]
["JP2","-","Pull Box",1,0.5,{"v":0.12154319321914336,"d":"0.12"},{"v":0.23083377240000005,"d":"0.23"},{"v":-0.10929057918085669,"d":"0.1093"},1,2,null,6]
["JP3","-","Pull Box",1,0.5,{"v":0.12154319321914336,"d":"0.12"},{"v":0.111503238,"d":"0.11"},{"v":0.01003995521914336,"d":"0.0100"},0.5,2,2]
["Pull Box","-","Booth",1,2,{"v":1.3422420054943205,"d":"1.34"},{"v":0.4447822302,"d":"0.44"},{"v":0.8974597752943205,"d":"0.8975"},1.25,33]
["Booth","-","Amp Rack",2,2,{"v":2.684484010988641,"d":"2.68"},{"v":1.5488504262000005,"d":"1.55"},{"v":1.1356335847886405,"d":"1.1356"},2.5,45,3,24]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[null,0,{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.0000"},0]
[]
["Conduit",null,"Size",null,0.5,0.75,1,1.25,1.5,2,2.5,3,3.5,4,4.5,5]
[null,null,"I.D.",null,0.622,{"v":0.8240000000000001,"d":"0.824"},1.049,{"v":1.38,"d":"1.380"},{"v":1.61,"d":"1.610"},2.067,2.469,3.068,3.548,4.026,4.506,5.047]
[null,null,"Fill area",0,0.12154319321914336,0.21330660135637838,{"v":0.3457011697602862,"d":"0.35"},0.5982849049496404,0.8143322317370103,1.3422420054943205,1.9151026294169886,2.957063040940298,3.954732336755501,5.092105744601719,6.378701033582271,8.00233046651038]
[null,null,"Fill Percent",40]
[]
["Cable",null,"Use",null,"Spk 1","Spk 2","Spk 4","Mic/line","CAT5e","Video","VGA","RG6","Biamp","Spk 3"]
[null,null,"Part number",null,224,225,227,291,4245,815,"819-5",841,77350,226]
[null,null,"O.D.",null,0.155,0.189,0.269,0.131,{"v":0.20800000000000002,"d":"0.208"},0.232,0.232,0.254,0.255,0.234]
[null,null,"Fill area",null,{"v":0.018869235,"d":"0.019"},{"v":0.0280552734,"d":"0.028"},{"v":0.056832329400000006,"d":"0.057"},{"v":0.013478249400000001,"d":"0.013"},{"v":0.03397954560000001,"d":"0.034"},{"v":0.0422733696,"d":"0.042"},{"v":0.0422733696,"d":"0.042"},{"v":0.0506708664,"d":"0.051"},{"v":0.051070634999999996,"d":"0.051"},{"v":0.043005362400000004,"d":"0.043"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"},{"v":0,"d":"0.000"}]
[null,null,"Quantity",null,1,1,1,1,1,1,5,1,1,1]
[null,null,"Description",null,"18 AWG TP","16 AWG TP","12 AWG TP","22 AWG STP","4 pr UTP","RG59 Coax","lo-loss RG59","CATV Coax","Biamp Conrol","14 AWG TP"]